## Slide 1
Enhancing Performance in EPICS Control System: Leveraging asyn/portDriver with Custom Device Support
April 15, 2024
Kukhee Kim for Algorithmic Data System SLAC National Accelerator Laboratory
2024 Spring EPICS Collaboration Meeting

## Slide 2: Abstract
2024 Spring EPICS Collaboration Meeting
The adoption of asyn/portDriver as a standard interface for EPICS (Experimental Physics and Industrial Control System) records has been integral to various control system projects at SLAC. Renowned for its stability, well-documented behavior, and reduced incidence of bugs, asyn/portDriver offers a straightforward and efficient means of developing EPICS drivers without necessitating extensive programming for device support. However, our endeavors revealed the necessity of crafting custom device support for specialized cases, such as the processing of records for Beam Synchronous Acquisition (BSA) and its associated services which requires EPICS IOC (Input/Output Controller) to manage and update a large volume of records with rapid rates. Consequently, we encountered heightened CPU load and performance degradation when operating numerous EPICS IOCs on a single server.
Our investigation into the elevated CPU load, memory footprint, and other performance metrics pertaining to BSA Process Variables (PVs) and their associated services involved a comparative analysis between asyn/portDriver and customized device support. Our findings demonstrated that custom device support yielded superior performance, with reduced CPU load and a smaller memory footprint. As a result, we transitioned to utilizing custom device support specifically for BSA and its related services, while retaining asyn/portDriver for most other generic records due to its myriad of benefits.
In this presentation, we share detailed insights gleaned from our test results and performance enhancements achieved through the adoption of custom device support. Additionally, we recount our successful experiences with asyn/portDriver, underscoring its continued relevance and efficacy in EPICS control systems.

## Slide 3: Contents
Control System Platform Changes for LCLS2
Standard Interfaces
  Common Platform Software
  Asyn port driver
Issues with new Platform
  Multiple iocs run on a single server
  Large memory consumption for LCLS2 BSA and related services
  Memory footprint
  Performance Issues
Using own device support to reduce memory footprint and better performance

## Slide 4: Control System Platform Changes in LCLS2
High Performance System (HPS)
  Real-Time Requirement: bunch by bunch response (sub-microseconds response), Timing System, Machine Protection, etc
  High bandwidth for data collecting from every bunch and aligning data across multiple systems including BPMs, LLRF, PCAV, XTCAV, etc
  Both may be required simultaneously
Platform Changes from VME/RTEMS to ATCA/LinuxRT
  Advanced Telecommunications Computing Architecture (ATCA)
  Hardware functions are implemented on AMC cards and RTM board
    Example of AMC cards: fast digitizer, RF up-converter and down-converter, etc
    Example of RTM cards: Debug RTM for timing interface and Ethernet, RF interlock RTM, etc
  Real-time requirements and Data Processing are implemented in FPGA firmware on the Carrier Board
    Examples including digital demodulation for RF system, digital phase lock loop for various applications, bunch by bunch feedback for RF system
  Software runs on LinuxRT CPU, meeting to minimum real-time requirements and provides EPICS PV interface
Non-HPS
  PCIe form factor, FPGA firmware-based system
  Examples including PCIe Timing Pattern Receiver (TPR), Frame Grabber with TPR, etc
  Real-Time requirements are implemented in Firmware
  Software provides minimum real-time requirements and provides EPICS interface

## Slide 5: ATCA Crate: Description
Air Intake Filter
Intake Fans
Power supply
DC or AC input
Shelf Manager
Almost all components can be replaced in the field (FRU).
Build around redundancy.
Exit Fans
Backplane
Slots for application cards (blades)

## Slide 6: ATCA Switch Card
Advantech ATCA-9112
Switches
  BI: Broadcom BCM56321 (24x1G)
  FI: Broadcom BCM56846 (24x10G)
Front panel
  8x SFP+ (FI)
  2x SFP+ (BI)
  Managment (1x LAN, 1x Conole)

## Slide 7: HPS: AMC daughter cards and RTM
MPS/Timing Rear Transition Module
Multi-use ADC/DAC AMC (MPS, BLEN, BCM)
Timing Digital AMC (Timing)
BPM AMC
Every card contains an EEPROM which contains information about the board
  Board type
  Serial number
  Personality options

## Slide 8: LCLS-II System example
Ethernet
Switch Card
Slot 1
Epics
Network
External
Timing
Network
IPMI
IPMI
Network
Carrier Board Slot 3
Carrier Board Slot 4
Carrier Board Slot 5
10/40 Gbps
Internal
Network
Timing
Distribution
IPMI
Busses Not
Shown
Carrier Board Slot 6
MPS
Update
Network
AMC 1
AMC 0
AMC 1
AMC 0
AMC 1
AMC 0
AMC 1
AMC 0
Carrier Board Slot 2
AMC 0
AMC 1
Standard off-the-shelf
“Dual Star” backplane
MPS
Update
Network
RTM
Linux Server
120VAC Power
10.x.y.103
10.x.y.104
10.x.y.105
10.x.y.106
10.x.y.102
10.x.y.1

## Slide 9: PCIe for Non-HPS (ex, PCIe TPR)
SFP port for LCLS-I
SFP port for LCLS-II
DSUB (DB-25)
TTL level trigger output
LEDs
PCIe Edge Connector
FPGA

## Slide 10: Modular Design and Standard Interface
Firmware and Software have been designed with the modular concepts
  Select and Reuse common firmware and software modules to develop the system
  Minimize new development
  Minimize potential bug and issues using proven modules
Standard Interfaces
  Common Platform Software (CPSW) for between Firmware and Software Interface
    Abstract Firmware Register and Memory, mmio as directory hierarchy with path names
    Abstract large DRAM space and messages from the firmware to a stream interface
    Abstract communication details and hardware interface: udp/RSSI for ATCA HPS, PCIe for Non-HPS, software doesn’t need to recognize different hardware platform
    Firmware uses yaml files to describe mmio and stream interface details, software downloads the yaml files during initialization and learns about the firmware
  Using asyn port Driver as standard PV interface
    Minimize development for the application driver (EPICS driver for application)
    Using proven code, Minimize potential bug
    No need to develop device support, short learning curve and less maintenance effort

## Slide 11: ATCA RF Common Platform Stack
Common Firmware Written in VHDL
Application Specific Firmware llrf_hls firmware
Window average
Channel weighted
Phase/Amplitude Feedback
Baseband RF profile
Application Specific Driver llrfHlsAsyn for LLRF Application
llrf_hls

## Slide 12: Software Stacks for modularization
Firmware
cpsw/framework
timing/hpsTpr
rf/llrfLib
Firmware/
Hardware
Software
EPICS Databases
EPICS Modules
API (non-epics)
tprTrigger
tprTrigger
db
tprPattern
tprPattern
db
BsaCore
BSA
Db Template
cpswLlrf
LlrfProc
LlrfProc
Db Template
cpswLlrf
Db Template
rf/ interlockRTM
rf/ common
atcaCommon
rfCommon
rfCommon Db Template
atcaCommon Db Template
atcaCommon
External Modules
External Modules
InterlockRTM
Bundled driver in ioc application
yamlLoader

## Slide 13: Performance/Resource Issues with the new Platform
A LinuxRT server hosts for multiple ATCA crates and operates multiple IOCs
Beam Synchronous Acquisition and its related services (BSA, BSSS, BSAS, BLD) requires large memory footprint and more processing
Large memory requirement and performance issue (high CPU load) are raised
Service | Definitions
BSA | Beam Synchronous Acquisition, Organizes data in Arrays, all aligned with the same pulse
BSSS | Beam Synchronous Scalar Service. Samples data with the BSA rates and publishes it as a single value
BSAS | Beam Synchronous Acquisition Service. Organizes statistical data in 2D table. There are common columns (timestamp, 64bit pulse id) and each data channel has columns for average, rms, minimum, maximum and delegate value. The table has 1k of rows to store time series of each column. It published as new EPICS7 NTTable PV. Mainly used by machine learning
BLD | Beam Line Data. Send data directly to a multicast network without sorting it. There is no PV to see the data contents. Mainly used by the photon side

## Slide 14: LCLS2 BSA Memory Consumptions (Buffer Memory for BSA PVs)
5 different history buffers for LCLS2 BSA, 40 bytes per sample
BSA history buffer PVs | Descriptions | Type | Size (Bytes)/Sample
mean | Average | Double | 8
cnt | Count | ULong | 8
rms | RMS | Double | 8
pidL | PID Lower Word | Ulong | 8
pidU | PID Upper Word | Ulong | 8
Total Byes per Sample |  |  | 40
50 EDEFs with 20,000 samples of buffer length
4 fault buffers with 1,000,000 samples of buffer length
EDEFs / Fault Buffer | Descriptions | Calculations
EDEFs | Bytes x EDEFs x 20,000 | 40 x 50 x 20,000 = 40MB (0.04GB)
Fault Buffers | Bytes x Fault Buffers x 1,000,000 | 40 x 4 x 1,000,000 = 160MB (0.16GB)
Total Bytes per BSA Channel |  | 0.04GB + 0.16GB = 0.2GB
0.2GB of memory requires for PVs of a single BSA channel
Example) If system has 12 BSA channels 12 x 0.2 GB = 2.4GB for for PVs a similar amount of memory requires for the bsaDriver to maintain the driver internal buffers Thus, 5.4GB of memory consumptions are expected

## Slide 15: SC Diagnostic Bus Input
Diagnostics Bus Inputs: BSA input for SC, firmware based BSA
  Data: 18bits or even more, if more than 18 bits are used, then the possibility for an overflow/underflow exists in the statistics calculations
  Fixed Input:
    Marked: the statistics are not computed, last valid input value will be advertised as the average
    Un-marked: firmware attempts to calculate the statistics
(18 bits)
(18 bits) x 2 = (36 bits)
(18 bits) + (13 bits) = (31 bits)
(36 bits) + (13 bits) = (49 bits)
Remarks, max number of average is 8191
is mostly equivalent to (x 8192),
BSA Statistics, DSP48 (48 bits arithmetic) in firmware
Diagnostic Bus
Data
Fixed Input Flag
Output to the software

## Slide 16: Current Implementation in SC BSA and SC BSAS
Mean and (n-1) Standard Deviation
BSA Implementation, Firmware/API/BSA Driver Separation
BSAS Implementation, Firmware/API/BSAS Driver Separation
The firmware provides yellow portion, the API provides green portion and all other portion is done by the bsaDriver.
The firmware provides yellow portion, and all other portion is done by the bsasDriver.

## Slide 17: Performance Issue on BSA driver
Symptoms
  Extending 44 Edefs for BSSS makes extra load, especially for TPG which has 31 data channels,
  a single thread could not catch up the BSSS processing (15 system Edefs with 31 data channels)
  The busy BSSS/BSAS/BLD listener thread makes fragile for the CPSW communication
Improvement
  Using multiple processing queue and worker threads to implement parallel processing
  The listener thread recognize the packet type and dispatches the data pointer to a proper queue/worker thread
  Using free list for the buffer and zero copy buffer to avoid overhead on the queueing
    Allocate 4 worker threads for BSSS
    Allocate 1 worker thread for BSAS
    Allocate 1 worker thread for BLD
  Parallelizing BSSS is easy, but need more consideration for BSAS (ex, waiting all rows are updated in the buffer, then post out the table into PVXS)

## Slide 18: Cont’d Performance Issue: Listener and Worker thread
Listener
CPSW UDP Thread
Dispatcher
Work Q for BLD
Worker Thread for BLD
Work Q for BSAS
Worker Thread for BSAS
Work Q0 for BSSS
Worker Thread0 for BSSS
Work Q1 for BSSS
Worker Thread1 for BSSS
Work Q2 for BSSS
Worker Thread2 for BSSS
Work Q3 for BSSS
Worker Thread3 for BSSS
The dispatcher uses
round-robin for the BSSS threads (parallel processing)

## Slide 19: Cont’d Performance Issue: CPU Load for the Listener and Worker Threads
PID PPID TID RTPRIO TIME %CPU STAT COMMAND WCHAN WCHAN
-----------------------------------------------------------------------
1864 1863 2113 79 00:00:07 1.3 SLsl+ bldStrm_root_0 - -
1864 1863 2114 64 00:02:50 31.1 SLsl+ bsssQ0_root_0 - -
1864 1863 2115 64 00:02:45 30.3 SLsl+ bsssQ1_root_0 - -
1864 1863 2116 64 00:02:53 31.6 SLsl+ bsssQ2_root_0 - -
1864 1863 2117 64 00:02:45 30.3 SLsl+ bsssQ3_root_0 - -
1864 1863 2119 64 00:00:06 1.2 SLsl+ bsasQ0_root_0 - -
1864 1863 2120 10 00:00:00 0.0 SLsl+ taskwd - -
(%CPU) > 100%
bsssQ<n>

## Slide 20: Cont’d Performance Issues: Monitoring Pending Queue and its Water-marker
sioc-b084-ts01>dbior bldStreamDriver
Driver: bldStreamDriver
BLD Stream for root_0
read size : 768
read count : 95387403
bld count : 0
bsss count : 4542715
bsas count : 90844688
else count : 0
bld callback : (nil)
bld_usr : (nil)
bsss_callback: 0x6c2d90
bsss_usr : 0x2ff8960
bsas_callback: 0x6c95c0
bsas_usr : 0x2e0a2d0
free list : 0x30bfa30
bldQueue[0]
name of thread: (null)
pending count : 0
water mark : 0
fail count : 0
overrun count : 0
bsssQueue[0]
name of thread: bsssQ0_root_0
pending count : 0
water mark : 1
fail count : 0
overrun count : 0
bsssQueue[1]
name of thread: bsssQ1_root_0
pending count : 0
water mark : 1
fail count : 0
overrun count : 0
bsssQueue[2]
name of thread: bsssQ2_root_0
pending count : 0
water mark : 1
fail count : 0
overrun count : 0
bsssQueue[3]
name of thread: bsssQ3_root_0
pending count : 0
water mark : 1
fail count : 0
overrun count : 0
bsasQueue[0]
name of thread: bsasQ0_root_0
pending count : 1
water mark : 8
fail count : 0
overrun count : 0

## Slide 21: Consideration for number of ioc vs. number of CPU cores
Generic Application (AmcCarrierTpr)
  Accumulated Average CPU load
  Required Core per ioc
    3 cores = 2 cores x 1.5 (safety factor)
  Generic ioc requires 3 cores per ioc
TPG Application (AmcCarrierTimingGenerator)
  Accumulated Average CPU load
  Required Core per ioc
    3.45 cores = 2.25 cores x 1.5 (safety factor)
  TPG requires approximately 4 cores per ioc
(%CPU) ≈ 185%
Threads for AmcCarrierTpr
(%CPU) ≈ 225%
Thread for AmcCarrierTimingGenerator
Test stand servers (cpu-b084-ts01, cpu-b084-sp18) have 5 cores CPU at 1.9GHz
The production servers have few configurations:
6 cores model has 1.9GHz
8 cores model has 1.7GHz
Since, the production servers have similar clock speed to the test stand, the estimation (number of cores per ioc) is still valid for the production.

## Slide 22: Scenario for the number of ioc vs. Number of cores
1 Crate (7 slots ATCA crate) + 1 Server Configuration
  6 AMC Carriers, thus 6 iocs are in the system
  Required CPU cores: 18 cores = 6 iocs x 3 cores/ioc
2 Crates (7 slots ATCA crate) + 1 Server Configuration
  12 AMC Carriers = (2 crate x 6 AMC Carrier/crate), thus 12 iocs should be in the system
  Require CPU cores: 36 cores = 12 iocs x 3 cores/ioc

## Slide 23: Cont’d Performance Issues: Record Processing and Bsa Poll
Relatively High CPU load for the Record Processing
  Separate out Record Processing to two callbacks
    cbLow: BSA PVs, Fault Buffers and All others
    cbMedium: BSSS exclusively
High CPU load on BSA poll thread
  The poll thread in TPG > 50%
  The poll thread in Amc TPR < 35%
  Good candidate to make parallel processing, but need some changes on the API layer to make it ready for the parallel processing
  Keep eyes on it, but no need to make change right now
PID PPID TID RTPRIO TIME %CPU STAT COMMAND WCHAN WCHAN
-----------------------------------------------------------------------
1864 1863 2122 58 00:29:23 3.8 SLsl+ cbLow - -
1864 1863 2123 63 01:55:51 15.1 RLsl+ cbMedium - -
1864 1863 2124 70 00:00:00 0.0 SLsl+ cbHigh - -
1864 1863 2125 50 00:00:00 0.0 SLsl+ dbCaLink - -
1864 1863 2126 50 00:00:00 0.0 SLsl+ PVAL - -
1864 1863 2127 50 00:05:30 0.7 SLsl+ serviceDrvPoll 1 hrtimer_nanosleep
1864 1863 2128 50 06:50:57 53.6 SLsl+ bsaDrvPoll 1 hrtimer_nanosleep
1864 1863 2129 98 00:00:26 0.0 SLsl+ tpgIrqPollingTa 1 hrtimer_nanosleep
1864 1863 2130 89 00:12:40 1.6 SLsl+ tpgSoftPollingT 1 hrtimer_nanosleep
1864 1863 2131 50 00:25:27 3.3 SLsl+ tpgBsaPollingTa 1 hrtimer_nanosleep
1864 1863 2132 10 01:14:48 9.7 RLsl+ tpgRateMeasureP - -
1864 1863 2133 10 00:02:32 0.3 SLsl+ tpgDiagnosticsT 1 hrtimer_nanosleep
1864 1863 2134 57 00:00:03 0.0 SLsl+ timerQueue - -
1864 1863 2135 50 00:00:00 0.0 SLsl+ devSeqCarScan 1 hrtimer_nanosleep
1864 1863 2136 19 00:00:00 0.0 SLsl+ PDB-event - -
1864 1863 2137 35 00:00:02 0.0 SLsl+ pvAccess-client - -

## Slide 24: Cont’d Performance Issue: Checking up Pending Queue and Water-Mark for Record Processing Callbacks
sioc-b084-ts01>callbackQueueShow()
PRIORITY HIGH-WATER MARK ITEMS IN Q Q SIZE % USED Q OVERFLOWS
cbLow 1387 0 12000 0.0 0
cbMedium 68 0 12000 0.0 0
cbHigh 0 0 12000 0.0 0
No pending queue count for cbLow and cbMedium,
but there are some water-mark.
Probably, the water mark comes from the burden during the iocInit()
we need to adjust the queue size to give enough headroom
(we have adjusted the queue size to 12,000 for TPG)
Consideration for Parallel Callback
We have tried to use Parallel Callback for the record processing in TPG,
found a few issues:
Record processing are stop without any precursor: suspect deadlock
Shows double free exception
We are not sure, the issues are caused by our side (API or epics driver modules which we developed), or epics base. Need more time for debugging

## Slide 25: Backup: Study for the Overhead of Asyn Port Driver for the BSSS
Compare CPU load before/after comment out the aysn port driver API calling for BSSS Scalar PV update in the Worker Threads
  1 time of setInteger64Param() for PID PV update
  2 times of setDoubleParam() for Scalar PV update
  1 time of callParamCallbacks() to make record processing
PID PPID TID RTPRIO TIME %CPU STAT COMMAND WCHAN WCHAN
-----------------------------------------------------------------------
1864 1863 2113 79 00:00:07 1.3 SLsl+ bldStrm_root_0 - -
1864 1863 2114 64 00:02:50 31.1 SLsl+ bsssQ0_root_0 - -
1864 1863 2115 64 00:02:45 30.3 SLsl+ bsssQ1_root_0 - -
1864 1863 2116 64 00:02:53 31.6 SLsl+ bsssQ2_root_0 - -
1864 1863 2117 64 00:02:45 30.3 SLsl+ bsssQ3_root_0 - -
1864 1863 2119 64 00:00:06 1.2 SLsl+ bsasQ0_root_0 - -
1864 1863 2120 10 00:00:00 0.0 SLsl+ taskwd - -
(%CPU) > 120%
bsssQ<n>
PID PPID TID RTPRIO TIME %CPU STAT COMMAND WCHAN WCHAN
-----------------------------------------------------------------------
3377 3376 3616 79 00:00:06 1.3 SLsl+ bldStrm_root_0 - -
3377 3376 3617 64 00:00:00 0.0 SLsl+ bsssQ0_root_0 - -
3377 3376 3618 64 00:00:00 0.0 SLsl+ bsssQ1_root_0 - -
3377 3376 3619 64 00:00:00 0.0 SLsl+ bsssQ2_root_0 - -
3377 3376 3620 64 00:00:00 0.0 SLsl+ bsssQ3_root_0 - -
3377 3376 3622 64 00:00:05 1.1 SLsl+ bsasQ0_root_0 - -
3377 3376 3623 10 00:00:00 0.0 SLsl+ taskwd - -
(%CPU) ≈ 0%
bsssQ<n>
Before
After
Most of CPU load for the BSSS operation comes from the overhead of asyn port driver
We can reduce most of CPU load on the BSSS worker thread with using own device support, instead of the using asyn port driver.

## Slide 26: Using own Device Support for BSSS and BSA
Overhead of the asyn port driver
  Performance dragging on BSSS worker thread and BSA poll thread – heavy overhead on set value/waveform to PV and queueing callback
  Performance dragging on cbLow and cbMedium callback – heavy overhead on record processing, especially large number of scalar PV update with relatively high rates
Own Device Support for BSSS and BSA
  Enhance the performance only executes the necessary instructions
  Using Zero copy buffer to avoid memcpy() for the buffer copy – performance improvement
  Free the pre-allocated memory buffer for waveform record, since using the Zero copy buffer
  Make NORD work with camonitor, the NORD can be used for the indication for the BSA PV is ready to read
Reduce the accumulate CPU usage
  TPG: 225% to 40%
  AmcCarrierTpr: 185% to 20%
Reduce Memory footprint: reduce ~3.6GB (for 31 BSA data source channels)

## Slide 27: Improvement on TPG
(%CPU) ≈ 225%
Thread for AmcCarrierTimingGenerator
(%CPU) ≈ 40%
Thread for AmcCarrierTimingGenerator
Using asyn port driver
Using own device support
Memory footprint for data session: 10.58GB
Memory footprint for data session: 6.94GB
Captured from /proc/<pid>/status
Captured from /proc/<pid>/status

## Slide 28: Improvement on AmcCarrierTpr
(%CPU) ≈ 185%
Thread for AmcCarrierTpr
(%CPU) ≈ 20%
Thread for AmcCarrierTpr
Using asyn port driver
Using own device support
Memory footprint for data session: 10.55GB
Memory footprint for data session: 6.95GB
Captured from /proc/<pid>/status
Captured from /proc/<pid>/status

## Slide 29: Summary
The LCLS2 control system has been developed on a new platform, featuring an ATCA-based HPS and PCIe-based Non-HPS architecture.
This innovative platform allows multiple IOCs to operate on a single server, streamlining operations.
Additionally, LCLS2 BSA and its associated services necessitate significant memory consumption and increased software processing.
These factors have led to memory footprint and performance issues on the new platform.
To address these challenges, we implemented modularization in both firmware and software components, utilizing standard interfaces such as CPSW for firmware/software communication and asyn/portDriver for managing EPICS records and PVs.
However, we discovered that the asyn/portDriver solution lacked the necessary memory footprint and performance capabilities for handling BSA and its related services.
By replacing the asyn/portDriver with custom device support tailored specifically for BSA and its services, we were able to reduce memory footprint and significantly improve overall performance.
Nonetheless, we continue to leverage asyn/portDriver for managing generic EPICS records, recognizing its myriad benefits and advantages over alternative solutions.