## Slide 1
Ralph Lange, ITER Organization
Device Support Spring 2024 Update

## Slide 2: OPC UA Features
Symbolic addressing
  names, not numbers
No PLC programming
  keep contractors happy
Industrial standard
  one to connect them all
Portability
  at least Linux, Windows
User-defined structures
  for reusable PLC objects
Subscription mechanism
  update on change
Server-side queues
  handle bursts well
Browsing support
  find variables easily
Security (X.509)
  encrypt, sign, authenticate
Remote procedure calls
  with parameters and results

## Slide 3: Performance
Test in 2021 for ITER building automation integration
  Trying to verify realistic conditions
  3x the estimated size (500kB data, mixed types)
  On a mid-size Siemens S7-1516
  250ms sampling/publishing period
  No performance fine-tuning
Results:
  Fit for this purpose
  Best performance when using few large structures

## Slide 4: Limitations
Mostly found on the server end
  S7-1500: depends on the model (S/M/L) and data organization
  How many, how large, how often?
  Client-side fine tuning available e.g., “registering” items to cache server-side name resolution
  Servers separate from PLCs introduce additional latency
Found one limit in the UA SDK client
  LabView serving 600 arrays of 7500 doubles each (~36MB data) -> SDK client has a limit of ~16MB for the serializer workaround: 3 subscriptions of 200 arrays each

## Slide 5: History
Evaluation of client library options and Device Support prototype Bernhard Kuner (HZB/BESSY)
ITER use cases tested by F4E (Spain) and TCS (India)
  Against S7-1516/1518 embedded OPC UA server
  Against WinCC-OA embedded OPC UA server
Current implementation, using a design that allows integrating different low-level client libraries
Recent major contributions from PSI, HZB/BESSY and ESS

## Slide 6: Low-Level OPC UA Client Choices
Stable: Use of commercial C++ Client SDK by Unified Automation
  4k€ for source code and 1 year support (extend support: 20% per year) one developer/many products or many developers/one product
  Binaries can be deployed/distributed royalty-free
  Platforms: Windows and Linux
  Evaluation bundles available
  Newest versions (1.7.9 and 1.8) have issues
Experimental: Use of free open62541 SDK client libraries
  Work by Dirk Zimoch (PSI) and Carsten Winkler (HZB/BESSY)
  Not trivial to set up
  More complexity on the Device Support side
  Less documentation than the UA SDK

## Slide 7: Status
Requirements Specification v1.1: https://bit.ly/opcua-srs-11
Design done (no formal doc yet)
Implementation nearly complete
  All basic data types and arrays thereof (read/write/subscribe)
  Supporting all applicable EPICS record types (bidirectional outputs)
  User-defined structures (read/write/subscribe), timestamps from data
  Server-side queues, configurable connection behavior
  OPC UA Security (encrypt, sign, authenticate) Lots of testing help by Roland Fleischhauer (HZB/BESSY)
  Integrated end-to-end test against a software server Work by Ross Elliot and Karl Vestin (ESS)

## Slide 8: Users (as of 2022)
Facility | OPC UA Server | Status
ASIPP | LabVIEW | production
 | PLC Siemens S7-1500 | production
Australian Synchrotron | PLC Siemens S7-1500F | near production
BESSY II @HZB | PLC Siemens S7-1500 | production
 | Phoenix Contact | production
 | Softing uaGate | production
CHIMERA @CCFE | PLC Siemens S7-1500 | development
 | LabVIEW | development
ESS | PLC Siemens S7-1500F | production
 | ABB Power SCADA | near production
 | Siemens DESIGO | development
Fermilab | Kepware KEPServerEX | testing
 | PLC Siemens S7-400 | development
IPR | PLC Siemens S7-1500 | testing
ITER | PLC Siemens S7-1500 | production
 | Siemens WinCC OA | production
 | PCVue | production
KATRIN @KIT | LabVIEW | prototyping
PSI | PLC Siemens S7-1500 | development
Varian ProBeam | PLC Siemens S7 | production
 | PLC Beckhoff | production

## Slide 9: Roadmap
Started:
  Wiki pages: List of servers that have been integrated with “useful tricks” OPC UA users: This needs your help !!
Currently working on:
  Integration of (free) open62541 client library first part merged (v0.9.5); second part is in an open Pull Request; will be available in next release Work by Dirk Zimoch (PSI) and Carsten Winkler (HZB/BESSY)
  User Manual ~30% done: Integration of README files and Cheat Sheet work still on a branch; first merge for the next release

## Slide 10: Roadmap
Currently working on:
  Extend support for arrays Ensure that both client libraries handle both types of OPC UA arrays, add support for arrays of structures Work by Dirk Zimoch (PSI)
  Support for server-side run-time changes of OPC UA structures Work by Karl Vestin (ESS)
Soon (fall 2024):
  Support for OPC UA methods (remote execution of PLC code)

## Slide 11: Download
Under EPICS license
Upstream repository, Wiki pages, binaries (future manual): https://github.com/epics-modules/opcua
The GitHub download area has statically linked binaries containing the UA SDK client (i.e., shared libraries to link your IOCs against)
  Easy to use, fully functional, free forever
  Needs to match your Linux distro and EPICS Base versions